## Design Calcs
Don L. Love, Ph.D., P.E.
Carrier Refrigeration Compressors
Indicates Input Information
Comments Per Carrier:
1. 1 ton is equal to 1 BHP driver
2. The following is a model description:
[5 empty] | Maximum |  | No. of
|  | Model No. |  | Tons | Driver BHP |  | Cylinders
|  | 5F40 |  | 40 | 40 |  | 4
|  | 5F50 |  | 50 | 50 |  | 5
|  | 5F60 |  | 60 | 60 |  | 6
|  | 5H40 |  | 40 | 40 |  | 4
|  | 5H60 |  | 60 | 60 |  | 6
|  | 5H80 |  | 80 | 80 |  | 8
|  | 5H120 |  | 120 | 120 |  | 12
|  | 5F126 |  | 126 | 126 |  | 12
(Extended stroke but they do not make these anymore)
3. All compressors are rated on R-22 as follows:
Saturated suction temperature of 45 F, which is 90.72 psia
Saturated Condenser temperature of 90 F, which is 183.1 psia
4. To LOAD a compressor, take the back cap off and screw out to the maximum
5. Condenser out temperature for standard refrigeration units = atmospheric temp. Plus 30 F.
6. Contacts:
"Horris" at AI 800-743-6009 in Mid west
"Elvis" in Mesquite, Texas, 405-232-3297 (rolls over from Oklahoma)
Southwest in Ok.City - 405-632-4193
Design Comments:
1. Assume a Driver BHP which is the same as tons in R-22
2. Fix the suction saturation temperature desired for the operation
3. Fix the Condensing temperature desired.
4. Then look at calculated chiller duty and see if this is acceptable to the process operation for the chiller
5. If too low, then INCREASE the driver BHP until it is acceptable.
IF the calculated BHP is greater than the design BHP, then a larger driver is needed. This will show up as an error
comment on line 33 below.
Capacity Calculations of a Compressor
By | Don Love |  |  |  |  | Date | 2005-11-05
Description |  | Superior Pipeline Bear Creek Plant with Existing PEC Unit - Carrier on Propane - SUMMER OPER.
Model Number |  | 5H120
Driver BHP |  | 60 |  | Tons based on R-22 |  | 60 | (BHP = Tons for R-22 Rating)
Atmospheric Press., psia |  |  | 14.4
Conditions: | [6 empty] | Based on R-22 as the Standard for Rating
| 1. Suction Saturated Temp., F (Allows for Temp. Rise from Recirc. Oil) | [5 empty] | 45 | (Standard) | (From Chiller)
| 2. Suction Pressure, psia | [5 empty] | 90.72 | (Standard)
| 3. Condensing Temp., F | [5 empty] | 90 | (Standard)
| 4. Condensing Pressure, psia | [5 empty] | 183.1 | (Standard)
| 5. Compression Ratio | [5 empty] | 2.0183 | (Standard)
| 6. Rated Mbtu/hr | [5 empty] | 720
| 7. Tons | [5 empty] | 60
| 8. Btu/# at Suction | [5 empty] | 108.553
| 9. Btu/# at Condensing Temperature | [5 empty] | 36.158
| 10. Differential Btu/# | [5 empty] | 72.395
| 11. #/hr of R22 to Compressor | [5 empty] | 9945.4382
| 12. ACFM of R22 to Compressor | [5 empty] | 100.1615
| 13. Cp/Cv of R22 | [5 empty] | 1.18
| 14. Compressor Efficiency (@ 90% of Driver) | [5 empty] | 50 | (Typical)
Based on Pure Propane (3% C2/97%C3)
| 15. ACFM of Compressor | [5 empty] | 100.1615
| 16. Chiller Shell Saturation Temperature, F | [5 empty] | -6 | (Chiller Out Temp.)
| 17. Saturation Suction Pressure, psig | [5 empty] | 21.5962 | (Calculated from Chiller Shell Temp.)
| 18. Discharge Pressure, psig | [5 empty] | 297.0844
| 19. Discharge Temperature, F (Partially Cooled by Lubr. Oil Recirc.) | [5 empty] | 170.3025 | (Calculated with Oil Cooling)
| 20. Propane Suction Saturation Density, #/CF | [5 empty] | 0.19363 |  |  | Dens. = .0411/1000 x e ^(.0198*(460+Temp)) | 8.9892 | 8016.5232 | 454
| 21. #/hr of Propane Capacity | [5 empty] | 1163.6373
| 22. Saturated Suction Btu/# | [5 empty] | 276.6317
| 23. Atmospheric Temperature, F | [5 empty] | 100
| 24. Condensing Temperature, F | [5 empty] | 130
| 25. Condensing Pressure, psig | [5 empty] | 295.0844 | (Calculated from Condensing Temp.)
| 26. Saturated Condenser Btu/# | [5 empty] | 190.0231
| 27. Differential Enthalphy, Btu/# | [5 empty] | 86.6086
| 28. Duty on Chiller, Mbtu/hr - Maximum Rating for Compressor | [5 empty] | 100.781 | (Maximum Chiller Duty for Design)
| 29. Tons of Refrigeration- Maximum Rating for Compressor | [5 empty] | 8.3984
| 30. Actual Duty on Chiller, Based on Driver BHP - Mbtu/hr | [5 empty] | 100.781
| 31. Actual Tons , Based on Driver BHP | [5 empty] | 8.3984
| 32. Percent of Propane to Rating at R-22 | [5 empty] | 13.9974
| 33. Compressor Efficiency, Estimate (Polytropic) | [5 empty] | 50
| 34. Compression Ratio | [5 empty] | 8.5977 | (Max. Recommended is 9) |  | MMSCFD
| 35. Cp/Cv | [5 empty] | 1.14 |  |  | 0.24087
| 36. Operating BHP | [5 empty] | 35.0715
Note: Actual Temperature to Compressor is 10 F higher than shell temperature because the
recirculating oil heats up the inlet vapor.
Also, if the oil cooling is by REINJECTING refrigerant to the inlet, then the #/hr of refrigerant
compressed is increased about 10% along with the operating BHP being higher. This is for
very small compressor applications only. Not normally used for Carrier Machines.

## Example Calcs
Example Calculations
D. Love
Reference: Carrier Compressor Company
Rating for a compressor is: | 5F40 means a 40 ton (4 cylinder ) compressor (Based on R-22)
5F60 means a 60 ton (6 cylinder ) compressor (Based on R-22)
5H120 means a 120 ton compressor
Rating is based on:
R22 Refrigerant
Suction, psia = 68 psia (30 F)
Discharge = 312 psia (Cooler outlet at 130 F)
Compression Ratio is 312/68 = 4.59 MAXIMUM for rod loading
Air In Temp. Plus 30 F = Air Condender Temp. Out.
Cooler | Temp. Out for Freon = 130 F
Example Propane Equivalent to R22 for 5F40/50 as Follows: | Cooler out temp. of 120 F = 242 psia for propane
Suction Pressure for Propane = 242 / Rc of 4.59 (for rod loading)
= 52.7 psia
| Therefore, for a Carrier Compressor, the suction temp. would be about 20 F | Equivalent Propane Temperature would be 17 F for the 52.7 psia
limited to rod loading.
For R22:
Example Capacity For 5F40/50:
Out of Chiller at 30 F, 68 psia = 107.284 Btu/# Total Enthalpy
To LCV or JT Valve at 130 F, 312 psia = 49.059 Btu/#
| For Propane: Out of Chiller at 20 F, about 52.7 psia = 197.3 Btu/# |  | Difference in Enthalpy = 58.2 Btu/#
To LCV or JT Valve at 120 F, 242 psia = 97.6
| Per 100 Mbtu/hr: |  | Difference in Enthalpy = 93.7 Btu/#
R22 = 100 x 1000 / 58.2 = 1,718.2 #/hr
Propane = 100 x 1000 / 93.7 = 1,067.2 #/hr
Freon ACFM = 1,718.2 * .782 Cu.Ft./# /60 = 22.4 ACFM (Capacity of Compressor)
Propane Equivalent ACFM = 1,067.2 * 1.876 cf./# / 6- = 33.4 ACFM
Therefore, the amount of propane that can be circulated through the compressor
= 22.4 / 33.4 = 67% of the amount of R22
Summary:
1. For R22, #/hr of Refrig. PER 100 Mbtu/hr = 1,718.2 (22.4 ACFM)
2. For Propane, #/hr of Refrig. PER 100 Mbtu/hr = 67% of 1,718.2 = 1,151 (22.4 ACFM)
BHP | Freon = BHP/MM Btu/hr = 175.65 (M.Wt. of 86.48 and Cp/Cv of 1.18)
Propane = BHP/MM Btu/hr = 140.03 (M.Wt. of 44 and Cp/Cv of 1.14)
Or 20% more BHP for Propane than for R22